Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 23 33 00 - AIR DUCT ACCESSORIES

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section Includes:

Manual volume dampers.

Flange connectors.

Turning vanes.

Duct-mounted access doors.

Flexible connectors.

Flexible ducts.

Duct accessory hardware.

ACTION SUBMITTALS

Product Data:  For each type of product.

For duct silencers, include pressure drop and dynamic insertion loss data.  Include breakout noise calculations for high transmission loss casings.

Shop Drawings:  For duct accessories.  Include plans, elevations, sections, details and attachments to other work.

Detail duct accessories fabrication and installation in ducts and other construction.  Include dimensions, weights, loads, and required clearances; and method of field assembly into duct systems and other construction.  Include the following:

Special fittings.

Manual volume damper installations.

Control-damper installations.

Retain "Wiring Diagrams" Subparagraph below if equipment includes wiring.

Wiring Diagrams:  For power, signal, and control wiring.

INFORMATIONAL SUBMITTALS

Retain "Coordination Drawings" Paragraph below for situations where limited space necessitates maximum utilization for efficient installation of different components or if coordination is required for installation of products and materials by separate installers.  Preparation of coordination drawings requires the participation of each trade involved in installations within the limited space.

Coordination Drawings:  Reflected ceiling plans, drawn to scale, on which ceiling-mounted access panels and access doors required for access to duct accessories are shown and coordinated with each other, using input from Installers of the items involved.

Retain "Source quality-control reports" Paragraph below if retaining "Source Quality Control" Paragraph in "Duct Silencers" Article.

Source quality-control reports.

CLOSEOUT SUBMITTALS

Operation and Maintenance Data:  For air duct accessories to include in operation and maintenance manuals.

PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products.  For an explanation of options and Contractor's product selection procedures, see SECTION 016000 "Product Requirements."

ASSEMBLY DESCRIPTION

Comply with NFPA 90A, "Installation of Air Conditioning and Ventilating Systems," and with NFPA 90B, "Installation of Warm Air Heating and Air Conditioning Systems."

Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" for acceptable materials, material thicknesses, and duct construction methods unless otherwise indicated.  Sheet metal materials shall be free of pitting, seam marks, roller marks, stains, discolorations, and other imperfections.

MATERIALS

Galvanized Sheet Steel:  Comply with ASTM A 653/A 653M.

Galvanized Coating Designation:  G90.

Exposed-Surface Finish:  Mill phosphatized.

Stainless-Steel Sheets:  Comply with ASTM A 480/A 480M, Type 304, and having a No. 2 finish for concealed ducts and finish for exposed ducts.

Reinforcement Shapes and Plates:  Galvanized-steel reinforcement where installed on galvanized sheet metal ducts; compatible materials for aluminum and stainless-steel ducts.

Tie Rods:  Galvanized steel, 1/4-inch minimum diameter for lengths 36 inches or less; 3/8-inch minimum diameter for lengths longer than 36 inches.

MANUAL VOLUME DAMPERS

Show dampers on Drawings.  If both standard and low-leakage volume dampers are required, identify each damper type on Drawings.

Standard, Steel, Manual Volume Dampers:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

Nailor Industries Inc.

Pottorff.

Ruskin Company.

Trox USA Inc.

Standard leakage rating.

Suitable for horizontal or vertical applications.

Frames:

Frame:  Hat-shaped, 20-gage, galvanized sheet steel.

Mitered and welded corners.

Flanges for attaching to walls and flangeless frames for installing in ducts.

Blades:

Multiple or single blade.

Parallel- or opposed-blade design.

Stiffen damper blades for stability.

Galvanized-steel, 0.064 inch thick.

Blade Axles:  Plated steel.

Bearings:

Molded synthetic.

Dampers in ducts with pressure classes of 3-inch wg or less shall have axles full length of damper blades and bearings at both ends of operating shaft.

Tie Bars and Brackets:  Galvanized steel.

Retain "Standard, Aluminum, Manual Volume Dampers" Paragraph below for aluminum ducts.  Coordinate with "Installation" Article and Section 233113 "Metal Ducts."

FLANGE CONNECTORS

If permitted by authorities having jurisdiction, flange connectors can substitute for slip-and-drive connections for smoke and combination fire and smoke dampers.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

Ductmate Industries, Inc.

Nexus PDQ; Division of Shilco Holdings Inc.

Ward Industries, Inc.; a division of Hart & Cooley, Inc.

Description:  Roll-formed, factory-fabricated, slide-on transverse flange connectors, gaskets, and components.

Material:  Galvanized steel.

Gage and Shape:  Match connecting ductwork.

If Project has more than one type or configuration of duct silencer, delete "Capacities and Characteristics" Paragraph below and schedule duct silencers on Drawings.

TURNING VANES

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

Ductmate Industries, Inc.

Duro Dyne Inc.

METALAIRE, Inc.

SEMCO Incorporated.

Retain "Manufactured Turning Vanes for Metal Ducts" and "Manufactured Turning Vanes for Nonmetal Ducts" paragraphs below for manufactured turning vanes.  Delete for turning vanes fabricated by Installer.

Manufactured Turning Vanes for Metal Ducts:  Curved blades of galvanized sheet steel; support with bars perpendicular to blades set; set into vane runners suitable for duct mounting.

Acoustic Turning Vanes:  Fabricate airfoil-shaped aluminum extrusions with perforated faces and fibrous-glass fill.

Manufactured Turning Vanes for Nonmetal Ducts:  Fabricate curved blades of resin-bonded fiberglass with acrylic polymer coating; support with bars perpendicular to blades set; set into vane runners suitable for duct mounting.

General Requirements:  Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible"; Figures 4-3, "Vanes and Vane Runners," and 4-4, "Vane Support in Elbows."

Retain one of two "Vane Construction" paragraphs below.

Vane Construction:  Double wall.

DUCT-MOUNTED ACCESS DOORS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

Ductmate Industries, Inc.

Greenheck Fan Corporation.

Pottorff.

Duct-Mounted Access Doors:  Fabricate access panels according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible"; Figures 7-2, "Duct Access Doors and Panels," and 7-3, "Access Doors - Round Duct."

Door:

Double wall, rectangular.

Galvanized sheet metal with insulation fill and thickness as indicated for duct pressure class.

Vision panel.

Hinges and Latches:  1-by-1-inch butt or piano hinge and cam latches.

Fabricate doors airtight and suitable for duct pressure class.

Frame:  Galvanized sheet steel, with bend-over tabs and foam gaskets.

Number of Hinges and Locks:

Access Doors Less Than 12 Inches Square:  No hinges and two sash locks.

Access Doors up to 18 Inches Square:  Continuous and two sash locks.

Access Doors up to 24 by 48 Inches:  Continuous and two compression latches with outside and inside handles.

Access Doors Larger Than 24 by 48 Inches:  Continuous and two compression latches with outside and inside handles.

DUCT ACCESS PANEL ASSEMBLIES

Retain this article for access panels in fire-rated duct systems, such as exhaust ducts for commercial kitchen hoods.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

Ductmate Industries, Inc.

Flame Gard, Inc.

3M.

Labeled according to UL 1978 by an NRTL.

Panel and Frame:  Minimum thickness 11-gage carbon steel.

Fasteners:  Carbon steel.  Panel fasteners shall not penetrate duct wall.

Gasket:  Comply with NFPA 96; grease-tight, high-temperature ceramic fiber, rated for minimum 2000 deg F.

Minimum Pressure Rating:  10-inch wg, positive or negative.

FLEXIBLE CONNECTORS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

Ductmate Industries, Inc.

Duro Dyne Inc.

Ward Industries, Inc.; a division of Hart & Cooley, Inc.

Materials:  Flame-retardant or noncombustible fabrics.

Coatings and Adhesives:  Comply with UL 181, Class 1.

Coordinate first five paragraphs below with "Installation" Article.  Delete "Metal-Edged Connectors" Paragraph if Contractor is allowed to shop fabricate metal-edged connector or if metal-edged connector is not necessary.

Metal-Edged Connectors:  Factory fabricated with a fabric strip 3-1/2 inches wide attached to two strips of 2-3/4-inch- wide, 0.028-inch- thick, galvanized sheet steel or 0.032-inch- thick aluminum sheets.  Provide metal compatible with connected ducts.

Connector fabric in "Indoor System, Flexible Connector Fabric" Paragraph below is not suitable for exposure to sun, weather, or corrosive environments.  It is suitable for system temperatures from minus 10 to plus 200 deg F (minus 23 to plus 93 deg C).

Indoor System, Flexible Connector Fabric:  Glass fabric double coated with neoprene.

Minimum Weight:  26 oz./sq. yd..

Tensile Strength:  480 lbf/inch in the warp and 360 lbf/inch in the filling.

Service Temperature:  Minus 40 to plus 200 deg F.

Connector fabric in "Outdoor System, Flexible Connector Fabric" Paragraph below is suitable for exposure to sun, weather, and system temperatures from minus 10 to plus 250 deg F (minus 23 to plus 121 deg C).

FLEXIBLE DUCTS

UL 181 defines two categories of flexible ducts.  Ducts listed according to UL 181 must pass all UL 181 tests.  Air connectors listed according to UL 181 must pass most, but not all, UL 181 tests and are limited to lengths of 14 feet (4.3 m) or less.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

Flexmaster U.S.A., Inc.

McGill AirFlow LLC.

Ward Industries, Inc.; a division of Hart & Cooley, Inc.

Retain one of five "Noninsulated, Flexible Duct" paragraphs below.

Retain one of five "Insulated, Flexible Duct" paragraphs.

Insulated, Flexible Duct:  UL 181, Class 1, polyethylene film supported by helically wound, galvanized-steel wire; fibrous-glass insulation; aluminized vapor-barrier film.

Pressure Rating:  10-inch wg positive and 1.0-inch wg negative.

Maximum Air Velocity:  5500 fpm.

Temperature Range:  Minus 10 to plus 160 deg F.

LEED Prerequisite EA 2 requires that duct insulation R-value comply with ASHRAE/IESNA 90.1-2004 tables titled "Minimum Duct Insulation R-Value, Cooling and Heating Only Supply Ducts and Return Ducts" and "Minimum Duct Insulation R-Value, Combined Heating and Cooling Supply Ducts and Return Ducts."

Insulation R-value:  Comply with ASHRAE/IESNA 90.1.

Flexible Duct Connectors:

Clamps: Stainless-steel band with cadmium-plated hex screw to tighten band with a worm-gear action in sizes 3 through 18 inches, to suit duct size.

Non-Clamp Connectors: Adhesive plus sheet metal screws.

EXECUTION

INSTALLATION

Install duct accessories according to applicable details in SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" for metal ducts and in NAIMA AH116, "Fibrous Glass Duct Construction Standards," for fibrous-glass ducts.

Install duct accessories of materials suited to duct materials; use galvanized-steel accessories in galvanized-steel and fibrous-glass ducts, stainless-steel accessories in stainless-steel ducts, and aluminum accessories in aluminum ducts.

LEED Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1-2004, in which Section 6.4.3.3.3 - "Shutoff Damper Controls" restricts the use of backdraft dampers and requires control dampers for certain applications.  If applying for LEED certification, retain option, in first paragraph below, required by ASHRAE/IESNA 90.1-2004.

Install backdraft dampers at inlet of exhaust fans or exhaust ducts as close as possible to exhaust fan unless otherwise indicated.

To minimize duct noise generated by volume dampers, SMACNA recommends locating dampers at least two duct diameters from fittings and as far away as possible from outlets.

Install volume dampers at points on supply, return, and exhaust systems where branches extend from larger ducts.  Where dampers are installed in ducts having duct liner, install dampers with hat channels of same depth as liner, and terminate liner with nosing at hat channel.

Coordinate subparagraphs below with Section 233113 "Metal Ducts."

Install steel volume dampers in steel ducts.

Install aluminum volume dampers in aluminum ducts.

Set dampers to fully open position before testing, adjusting, and balancing.

Install test holes at fan inlets and outlets and elsewhere as indicated.

Install fire and smoke dampers according to UL listing.

Retain first paragraph below.

Connect ducts to duct silencers rigidly.

Install duct access doors on sides of ducts to allow for inspecting, adjusting, and maintaining accessories and equipment at the following locations:

On both sides of duct coils.

Upstream from duct filters.

At outdoor-air intakes and mixed-air plenums.

At drain pans and seals.

Downstream from manual volume dampers, control dampers, backdraft dampers, and equipment.

Adjacent to and close enough to fire or smoke dampers, to reset or reinstall fusible links.  Access doors for access to fire or smoke dampers having fusible links shall be pressure relief access doors and shall be outward operation for access doors installed upstream from dampers and inward operation for access doors installed downstream from dampers.

Retain first three subparagraphs below to provide access for duct cleaning.  LEED Prerequisite IEQ 1 requires compliance with ASHRAE 62.1-2004, in which Section 7.2.4 - "Ventilation System Start-Up" requires that distribution systems be clean of dirt and debris.

At each change in direction and at maximum 50-foot spacing.

Upstream from turning vanes.

Upstream or downstream from duct silencers.

Control devices requiring inspection.

Elsewhere as indicated.

Install access doors with swing against duct static pressure.

Sizes in "Access Door Sizes" Paragraph below are from one manufacturer's literature.  SMACNA lists only three sizes, 12 by 12 inches (300 by 300 mm), 16 by 20 inches (400 by 500 mm), and 24 by 24 inches (600 by 600 mm), but makes no recommendations for applications.  Indicate location and type of each access door on Drawings.

Access Door Sizes:

One-Hand or Inspection Access:  8 by 5 inches.

Two-Hand Access:  12 by 6 inches.

Head and Hand Access:  18 by 10 inches.

Head and Shoulders Access:  21 by 14 inches.

Body Access:  25 by 14 inches.

Body plus Ladder Access:  25 by 17 inches.

Coordinate first paragraph below with Section 230553 "Identification for HVAC Piping and Equipment."

Label access doors according to Section 230553 "Identification for HVAC Piping and Equipment" to indicate the purpose of access door.

Install flexible connectors to connect ducts to equipment.

For fans developing static pressures of 5-inch wg and more, cover flexible connectors with loaded vinyl sheet held in place with metal straps.

Retain first paragraph below to allow use of flexible duct to connect terminal units to metal duct.

Connect diffusers to ducts with maximum 60-inch lengths of flexible duct clamped or strapped in place.

Connect flexible ducts to metal ducts with draw bands.

Install duct test holes where required for testing and balancing purposes.

Retain paragraph below for thrust limits on flexible connections for fans.

Install thrust limits at centerline of thrust, symmetrical on both sides of equipment.  Attach thrust limits at centerline of thrust and adjust to a maximum of 1/4-inch movement during start and stop of fans.

FIELD QUALITY CONTROL

Tests and Inspections:

Operate dampers to verify full range of movement.

Inspect locations of access doors and verify that purpose of access door can be performed.

Operate fire, smoke, and combination fire and smoke dampers to verify full range of movement and verify that proper heat-response device is installed.

Inspect turning vanes for proper and secure installation.

Operate remote damper operators to verify full range of movement of operator and damper.

END OF SECTION 233300