SECTION 23 21 13

HYDRONIC PIPING

PART 1 - GENERAL

1.01	SUMMARY

A.	Section Includes:

1.	Chilled water piping and fittings.

2.	Heating hot water piping and fittings.

3.	Condenser water piping and fittings.

4.	Glycol solution piping and fittings.

5.	Piping specialties and accessories.

6.	Valves and valve accessories.

B.	Related Sections:

1.	Section 23 05 00 - Common Work Results for HVAC.

2.	Section 23 05 29 - Hangers and Supports for HVAC Piping and Equipment.

3.	Section 23 05 48 - Vibration and Seismic Controls for HVAC.

4.	Section 23 05 53 - Identification for HVAC Piping and Equipment.

5.	Section 23 07 19 - HVAC Piping Insulation.

6.	Section 23 21 23 - Hydronic Pumps.

1.02	REFERENCES

A.	American Society of Mechanical Engineers (ASME):

1.	ASME B1.20.1 - Pipe Threads, General Purpose.

2.	ASME B16.1 - Gray Iron Pipe Flanges and Flanged Fittings.

3.	ASME B16.3 - Malleable Iron Threaded Fittings.

4.	ASME B16.5 - Pipe Flanges and Flanged Fittings.

5.	ASME B16.9 - Factory-Made Wrought Buttwelding Fittings.

6.	ASME B16.11 - Forged Fittings, Socket-Welding and Threaded.

7.	ASME B16.22 - Wrought Copper and Copper Alloy Solder Joint Pressure Fittings.

8.	ASME B31.9 - Building Services Piping.

B.	ASTM International:

1.	ASTM A53/A53M - Standard Specification for Pipe, Steel, Black and Hot-Dipped, Zinc-Coated, Welded and Seamless.

2.	ASTM A106/A106M - Standard Specification for Seamless Carbon Steel Pipe for High-Temperature Service.

3.	ASTM B88 - Standard Specification for Seamless Copper Water Tube.

4.	ASTM B280 - Standard Specification for Seamless Copper Tube for Air Conditioning and Refrigeration Field Service.

C.	American Welding Society (AWS):

1.	AWS A5.8 - Specification for Filler Metals for Brazing and Braze Welding.

2.	AWS D1.1 - Structural Welding Code - Steel.

1.03	DEFINITIONS

A.	Finished Spaces: Spaces with ceilings, finished walls, and floor coverings.

B.	Exposed: Visible in occupied spaces, mechanical rooms, and service areas.

C.	Concealed: Hidden above ceilings, within walls, chases, or in shafts.

D.	NPS: Nominal Pipe Size.

E.	DN: Diameter Nominal (metric equivalent of NPS).

1.04	ACTION SUBMITTALS

A.	Product Data:

1.	Submit manufacturer's product data for each type of pipe, fitting, and valve.

2.	Include pressure-temperature ratings, materials of construction, and dimensions.

B.	Shop Drawings:

1.	Submit shop drawings for piping systems, including:

a.	Piping layout with sizes, elevations, and slopes.

b.	Hanger and support locations.

c.	Expansion loops and offsets.

d.	Equipment connections.

e.	Coordination with other trades.

2.	Submit isometric drawings for complex piping arrangements.

C.	Welding Certificates:

1.	Submit AWS certifications for welders.

2.	Submit welding procedure specifications (WPS).

1.05	INFORMATIONAL SUBMITTALS

A.	Welding certificates.

B.	Field quality-control reports.

C.	Pressure test reports.

1.06	QUALITY ASSURANCE

A.	Installer Qualifications:

1.	Piping contractor with minimum 5 years documented experience.

2.	Welders certified per AWS D1.1 or ASME Section IX.

B.	Regulatory Requirements:

1.	Comply with applicable codes:

a.	California Mechanical Code (CMC).

b.	California Plumbing Code (CPC).

c.	California Building Code (CBC).

d.	California Fire Code.

e.	ASME B31.9 for building services piping.

2.	Obtain required permits and inspections.

3.	For DSA projects:

a.	Comply with Division of the State Architect requirements.

b.	Provide continuous inspection for welded joints.

c.	Submit required DSA documentation.

1.07	DELIVERY, STORAGE, AND HANDLING

A.	Deliver piping and fittings in manufacturer's original packaging.

B.	Store materials in clean, dry location protected from weather.

C.	Protect pipe ends from damage and contamination.

D.	Store valves in closed position.

PART 2 - PRODUCTS

2.01	PIPING MATERIALS

A.	Steel Pipe:

1.	NPS 2 and smaller:

a.	ASTM A53/A53M, Type E or S, Grade B, Schedule 40, black.

b.	Threaded ends for fittings NPS 2 and smaller.

c.	Fittings: ASME B16.3, malleable iron, Class 150.

2.	NPS 2-1/2 and larger:

a.	ASTM A53/A53M, Type E or S, Grade B, Schedule 40, black.

b.	Welded or flanged connections.

c.	Fittings: ASME B16.9, wrought steel, butt-welding type.

d.	Flanges: ASME B16.5, forged steel, Class 150.

B.	Copper Tube:

1.	ASTM B88, Type L, hard drawn.

2.	Fittings:

a.	ASME B16.22, wrought copper, solder joint.

b.	ASME B16.18, cast copper alloy, solder joint.

3.	Joints:

a.	Solder: ASTM B32, lead-free, Alloy Sn95 or Sn96.

b.	Brazing: AWS A5.8, BCuP series.

c.	Flux: Types recommended by solder manufacturer.

2.02	VALVES

A.	General Valve Requirements:

1.	Pressure rating: 125 psig minimum working pressure.

2.	Temperature rating: Suitable for system operating temperatures.

3.	End connections to match piping system.

B.	Ball Valves:

1.	NPS 2 and smaller:

a.	Two-piece or three-piece body, full port.

b.	Bronze or brass body.

c.	Chrome-plated brass ball.

d.	TFE seats and seals.

e.	Blowout-proof stem.

f.	Lever handle with memory stop.

2.	NPS 2-1/2 and larger:

a.	Two-piece or three-piece body, full port.

b.	Carbon steel body, ASTM A216 Grade WCB.

c.	Stainless steel ball and stem.

d.	TFE seats and seals.

e.	Gear operator for NPS 4 and larger.

C.	Butterfly Valves:

1.	NPS 2-1/2 and larger:

a.	Lug style or wafer style body.

b.	Cast iron or ductile iron body.

c.	Aluminum bronze or stainless steel disc.

d.	EPDM seat for temperatures to 250°F.

e.	Gear operator for NPS 6 and larger.

f.	Memory stop.

D.	Check Valves:

1.	NPS 2 and smaller:

a.	Swing check, Class 125.

b.	Bronze body, bronze disc.

2.	NPS 2-1/2 and larger:

a.	Silent check or swing check.

b.	Cast iron body, bronze trim.

c.	Wafer style for silent check valves.

E.	Balancing Valves:

1.	Calibrated balancing valve with:

a.	Memory stop.

b.	Pressure/temperature test ports.

c.	Flow measurement capability.

2.	Manufacturers:

a.	Bell & Gossett (Circuit Setter).

b.	Tour & Andersson (STAD).

c.	Armstrong (CBV).

d.	Or approved equal.

2.03	PIPING SPECIALTIES

A.	Y-Type Strainers:

1.	Body: Cast iron or bronze, Class 125.

2.	Screen: Stainless steel, 20-mesh.

3.	Blowdown connection.

B.	Flexible Connectors:

1.	Stainless steel braided hose with carbon steel flanges.

2.	Working pressure: 150 psig minimum.

3.	Length: As required for equipment isolation.

C.	Expansion Joints:

1.	Packed slip type or bellows type as indicated.

2.	Anchors and guides per manufacturer's recommendations.

D.	Air Vents:

1.	Automatic air vents:

a.	Float type, brass body.

b.	Maximum pressure: 150 psig.

c.	Maximum temperature: 240°F.

d.	Provide isolation valve below each air vent.

2.	Manual air vents:

a.	Brass body with hose connection.

b.	Provide at high points where automatic vents are not indicated.

E.	Pressure/Temperature Test Plugs:

1.	Brass body with neoprene core.

2.	Provide at locations indicated and at each piece of equipment.

PART 3 - EXECUTION

3.01	EXAMINATION

A.	Verify building structure is ready to receive piping.

B.	Verify pipe chases and openings are correctly located and sized.

C.	Verify equipment is set and ready for piping connections.

D.	Report unsatisfactory conditions in writing; do not proceed until corrected.

3.02	PIPING INSTALLATION

A.	General Requirements:

1.	Install piping in accordance with ASME B31.9.

2.	Route piping parallel to building lines where possible.

3.	Install piping to permit:

a.	Valve operation and replacement.

b.	Access for maintenance.

c.	Expansion and contraction.

d.	Air venting at high points.

e.	Drainage at low points.

4.	Slope horizontal piping:

a.	Minimum 1 inch in 40 feet in direction of flow.

b.	Provide drains at low points.

c.	Provide vents at high points.

B.	Pipe Joints:

1.	Threaded joints:

a.	Cut threads per ASME B1.20.1.

b.	Ream pipe ends after cutting.

c.	Apply thread sealant to male threads only.

d.	Use PTFE tape or pipe dope suitable for system fluid.

2.	Welded joints:

a.	Perform welding per AWS D1.1 or ASME Section IX.

b.	Use qualified welders only.

c.	Remove slag and spatter.

d.	Clean interior of pipe after welding.

3.	Soldered joints:

a.	Clean tube and fittings before assembly.

b.	Apply flux to tube end only.

c.	Use lead-free solder.

d.	Wipe excess solder from joints.

C.	Valve Installation:

1.	Install valves with stems oriented as follows:

a.	Vertical, stem up, where possible.

b.	Horizontal stem acceptable.

c.	Stem down not permitted.

2.	Provide unions or flanges at each valve for removal.

3.	Provide access for valve operation and maintenance.

3.03	PRESSURE TESTING

A.	Test Requirements:

1.	Test piping systems before insulation is applied.

2.	Test pressure: 1.5 times the system design pressure, minimum 100 psig.

3.	Test duration: 2 hours minimum.

4.	Acceptance criteria: No visible leaks, no pressure drop.

B.	Test Medium:

1.	Hydrostatic test with water.

2.	Pneumatic test only where hydrostatic test is not practical.

C.	Procedure:

1.	Notify Engineer 48 hours prior to testing.

2.	Isolate equipment that cannot withstand test pressure.

3.	Fill system and vent air.

4.	Apply test pressure and hold for required duration.

5.	Repair leaks and retest until acceptable.

6.	Submit test reports.

3.04	CLEANING AND FLUSHING

A.	Clean interior of piping systems:

1.	Remove debris, scale, and foreign materials.

2.	Flush with clean water until discharge runs clear.

3.	Chemically clean if required by system design.

B.	Flushing Procedure:

1.	Open strainer blowdowns.

2.	Flush at minimum 2 fps velocity.

3.	Clean strainer screens after flushing.

4.	Drain system if freeze protection is not provided.

3.05	SYSTEM FILLING

A.	Fill systems with treated water per system requirements.

B.	Vent air from system at all high points.

C.	For glycol systems:

1.	Use premixed glycol solution.

2.	Glycol concentration as indicated on Drawings.

3.	Verify concentration after filling.

3.06	FIELD QUALITY CONTROL

A.	Inspection:

1.	Inspect piping installation before concealment.

2.	Verify compliance with contract documents.

B.	Welding Inspection:

1.	Visual inspection of all welds.

2.	Radiographic inspection where specified.

C.	Non-Conforming Work:

1.	Remove and replace non-conforming work.

2.	No additional cost to Owner.

END OF SECTION 23 21 13